## Slide 1
High-strength World's only flexible C-Si solar panels which can pass 35 mm hail test
Easy-to-install No need for PV support bracket, modules can be directly bonded to installation surface by weather-resistant glue
Aesthetics Module's surface and texture can be customized to meet aesthetic requirements
Low-weight Areal weight: 2.9 kg/m2, Less than 30% of traditional glass-based solar modules
Thin Thickness: 1.8 mm (junction box not included), Only 50% of traditional glass-based solar modules
Flexible Smallest bending radius of 0.3 m, No cell cracks and no power losses
Module type: ZKFN D1 000A Peak-power: 250W-260W
Quality Assurance
IEC61215, IEC61730
ISO9001:2015
中科富能
CAS FUTURE ENERGY
Standard Module Power Warranty
ZKFN Module Power Warranty
※1st year degradation less than 2.5%, 25 years power output 85.5% guaranteed.
Insured by CHINA RE
12year 25year
Quality Performance
Warranty Warranty
Reinsurance Coverage for 25 Years
Super-strength
Mono PERC Flexible Module
260W Max-Power | 22.0% Max-Efficiency | 0~+5W Power-selection
中科富能
CAS FUTURE ENERGY
Tel.：0086 400 6768 100 / 00866 199 0537 7053 Web.：www.zkfnsolar.com
Add.：Factory 1 of XinShenglin, LvHaiHui Intelligent Manufacturing Industrial Park, Jining Economic Development Zone, Jining, Shandong，China
山东中科富能光电科技有限公司
Shandong CAS Future Energy Photoelectric Technology Co., Ltd

## Slide 2
Size(mm)
Electrical performance parameters (STC* )
Curve characteristic diagram (265Wp)
I-V Curve
P-V Curve
Module Type |  |  | ZKFN D1 000A-250 | ZKFN D1 000A-255 | ZKFN D1 000A-260
Max-Power | PMPP | [W] | 250 | 255 | 260
Power selection |  | [W] | 0～5W | 0～5W | 0～5W
Max-Power Voltage | VMPP | [V] | 42.41 | 42.48 | 42.55
Max-Power Current | IMPP | [A] | 5.90 | 6.00 | 6.11
Open-Circuit Voltage | Voc | [V] | 49.68 | 49.75 | 49.82
Open-Circuit Voltage | Isc | [A] | 6.10 | 6.22 | 6.33
Max. series fuse rating |  | [A] | 25 |  | 
Max. system voltage | IEC/UL | [V] | 1500V DC |  | 
Note: Due to product update and technical improvement, the product technical parameters provided by Funeng components may be slightly different from this specification. Funeng reserves the right to adjust the technical parameters without notifying the customer. For the new technical parameter files, please see www.zkfnsolar.com. The final interpretation of the technical specifications shall be reserved by Zhongke Funeng.
Mechanical parameters
Cell Type | Mono PERC 182mm*182mm
Size | 1200*1146*1.8mm
Thickness | 1.8mm (junction box not included)
Weight | 2.9kg/㎡
Connector | MC4 Compatible
Junction-box | IP68
Backboard color | White
STC*: Irradiance=1000 W/m², Module temperature=25℃, AM=1.5，Test uncertainty for Pmax:±3%
Temperature coefficient
Temperature-coefflcient of PMPP | [%/℃] | -0.37
Temperature-coefflcient of Voc | [%/℃] | -0.28
Temperature-coefflcient of Isc | [%/℃] | 0.05
NOCT | [℃] | 45±2
Application parameters
Max. system voltage | DC1500V
Power selection | 0～+5W
Operating temperature range | -40℃～+85℃
Max. series fuse rating | 25A
Mechanical Load | 2400Pa